BladeCenter to HPI Mapping

April 28, 2006

# Introduction
BladeCenter HPI support is through the open source project – OpenHPI. OpenHPI supports HPI with a common set of core infrastructure code and a series of code plugins that are hardware and/or protocol specific. One of these plugins supports the IBM BladeCenter products.
HPI applications may run multiple plugins (e.g. to support ATCA and BladeCenter systems) or multiple instances of the same plugin (e.g. to support multiple BladeCenter chassis). For details on OpenHPI, refer to http://openhpi.sourceforge.net.
The OpenHPI BladeCenter plugin code communicates with the BladeCenter's Management Module using SNMP. No matter where the HPI application resides – on a laptop, on a standalone server, or on one of the blades in the BladeCenter itself – an external network path must exist to the BladeCenter's Management Module. The OpenHPI BladeCenter plugin mines the SNMP information available in the BladeCenter's SNMP MIB and translates that information into HPI structures, states, and events.
## OpenHPI BladeCenter Plugin Configuration File
The HPI BladeCenter plugin is configured with the OpenHPI file – openhpi/examples/openhpi.conf. Here's an example of the variables:

Variable	Default Value	Description
entity_root	“{SYSTEM_CHASSIS, 4}”	Defines the last part of each resource's Entity Path. {SAHPI_ENT_ROOT, 0} is assumed at the end of this definition. Applications can run multiple instances of the plugin to support multiple BladeCenters. To keep track of which BladeCenter is being addressed, change the location number (4) to a unique number for each plugin instance definition.
host	“192.168.70.125”	BladeCenter Management Module (MM) IP address.
version	“1”	SNMP version. SNMP versions 1 and 3 are supported.
community	“public”	SNMP v1 community name. Required if using SNMP v1; must match “Community Name” configured in the MM.
security_name	“snmpv3_user”	SNMP v3 user name. Required if using SNMP v3; must match one of the “Login IDs” configured in the MM.
context_name	“context_name”	SNMP v3 context name. Required if MM's “Context name” field is defined for the SNMP v3 “Login ID”.
security_level	“authNoPriv”	SNMP v3 security level. noAuthNoPriv, authNoPriv, and authPriv supported.
passphrase	“”	SNMP v3 authentication password. Required if using SNMP v3 and security_level is authNoPriv or authPriv; must match “Password” defined in MM for the SNMP v3 “Login ID”.
auth_type	“MD5”	SNMP v3 authentication password encoding type. Required if using SNMP v3 and security_level is authNoPriv or authPriv. Must match “Authentication Protocol” defined in the MM. Values of MD5, SHA, and None are supported.
privacy_passwd	“”	SNMP v3 privacy password. Must match “Privacy password” defined in the MM.
privacy_protocol	“None”	SNMP v3 privacy protocol. Must match “Privacy protocol” defined in the MM. Values of None and DES are supported. If security_level is authPriv, code defaults privacy_protocol to DES since there is currently no other privacy protocol choice.
count_per_getbulk	“32”	SNMP v3. Optional. SNMP_MSG_GETBULK commands can be used to increase performance. This variable sets the MAX OIDs allowable per MSG_GETBULK command. / A value of “0” disables the use of the SNMP_MSG_GETBULK SNMP command. / Positive values less than 16 default to “16”, since values less than 16 don't necessarily increase performance. / Too high of a value (> 40) can cause SNMP commands to BladeCenter to timeout. / Default is “32”.

1.1: OpenHPI BladeCenter Plugin Configuration Variables
## BladeCenter References
- In the spirit of open source, the best documentation source (and generally the most accurate) is the code. When you download the OpenHPI code, BladeCenter plugin code is located in the openhpi/plugins/snmp_bc directory. Two of the key files in that directory are:
- snmp_bc_resources.c - describes the Resources and RDRs supported.
- snmp_bc_event.map - describes which BladeCenter events are explicitly mapped to HPI events.
- BladeCenter Management Module code can be downloaded from http://www.ibm.com. Click on “Downloads and drivers”. When you download the code, you'll also get the BladeCenter's SNMP MIB.
- http://www-03.ibm.com/systems/bladecenter contains lots of good BladeCenter information.

# BladeCenter Resources
Table 2.1: BladeCenter Resources describes an abbreviated RPT table for supported BladeCenter resources.

Resource	Entity Path	Capabilities	Severity
BladeCenter Chassis	{entity_root}	SAHPI_CAPABILITY_CONTROL / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Virtual Management Module	{SAHPI_ENT_SYS_MGMNT_MODULE, 0} / {entity_root}	SAHPI_CAPABILITY_CONTROL / SAHPI_CAPABILITY_EVENT_LOG / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Management / Module Slot x	{BLADECENTER_SYS_MGMNT_MODULE_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Management / Module x	{SAHPI_ENT_SYS_MGMNT_MODULE, x} / {BLADECENTER_SYS_MGMNT_MODULE_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_MANAGED_HOTSWAP / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESET / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
Blade Slot x	{SAHPI_ENT_PHYSICAL_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Blade x	{SAHPI_ENT_SBC_BLADE, x} / {SAHPI_ENT_PHYSICAL_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_CONTROL / SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_MANAGED_HOTSWAP / SAHPI_CAPABILITY_POWER / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESET / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
Blade Expansion Module (BEM) x	{SAHPI_ENT_SYS_EXPANSION_BOARD, x} / {SAHPI_ENT_SBC_BLADE, x} / {SAHPI_ENT_PHYSICAL_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
BEM DASD	{SAHPI_ENT_DISK_DRIVE} / {SAHPI_ENT_SYS_EXPANSION_BOARD, x} / {SAHPI_ENT_SBC_BLADE, x} / {SAHPI_ENT_PHYSICAL_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
I/O Module Slot x	{BLADECENTER_INTERCONNECT_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
I/O Module x	{SAHPI_ENT_INTERCONNECT, x} / {BLADECENTER_INTERCONNECT_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_MANAGED_HOTSWAP / SAHPI_CAPABILITY_POWER / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESET / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
Power Module Slot x	{BLADECENTER_POWER_SUPPLY_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Power Module x	{SAHPI_ENT_POWER_SUPPLY, x} / {BLADECENTER_POWER_SUPPLY_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
Blower Slot x	{BLADECENTER_FAN_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_CRITICAL
Blower x	{SAHPI_ENT_FAN, x} / {BLADECENTER_FAN_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR
Media Tray Slot x	{BLADECENTER_PERIPHERAL_BAY_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE	SAHPI_CRITICAL
Media Tray x	{SAHPI_ENT_PERIPHERAL_BAY, x} / {BLADECENTER_PERIPHERAL_BAY_SLOT, x} / {entity_root}	SAHPI_CAPABILITY_FRU / SAHPI_CAPABILITY_INVENTORY_DATA / SAHPI_CAPABILITY_RDR / SAHPI_CAPABILITY_RESOURCE / SAHPI_CAPABILITY_SENSOR	SAHPI_MAJOR

Table 2.1: BladeCenter Resources
## BladeCenter non-Standard Entity Type Definitions
Unfortunately, the HPI B.01.01 standard does not support entity types for different types of hardware slots. To support various slot types, the OpenHPI BladeCenter plugin supports the following entity path extensions:
BladeCenter non-Standard Entity Path Definition	Value
BLADECENTER_INTERCONNECT_SLOT	SAHPI_ENT_CHASSIS_SPECIFIC + 0x10
BLADECENTER_POWER_SUPPLY_SLOT	SAHPI_ENT_CHASSIS_SPECIFIC + 0x11
BLADECENTER_PERIPHERAL_BAY_SLOT	SAHPI_ENT_CHASSIS_SPECIFIC + 0x12
BLADECENTER_SYS_MGMT_MODULE_SLOT	SAHPI_ENT_CHASSIS_SPECIFIC + 0x13
BLADECENTER_BLOWER_SLOT	SAHPI_ENT_CHASSIS_SPECIFIC + 0x14

Table 2.2: BladeCenter non-Standard Entity Path Definitions
These extensions are defined in the OpenHPI file SaHpiBladeCenter.h.
## Entity Path Examples
{entity_root} is defined in OpenHPI's openhpi.conf file. For example, if entity_root = “{SYSTEM_CHASSIS, 2}” in openhpi.conf, then {entity_root} is:
{SAHPI_ENT_SYSTEM_CHASSIS, 2}
{SAHPI_ENT_ROOT, 0}
For the following examples, assume entity_root = “{SYSTEM_CHASSIS, 1}” is defined in openhpi.conf.

Example 1: Blade in slot 3
{SAHPI_ENT_SBC_BLADE, 3}
{SAHPI_ENT_PHYSICAL_SLOT, 3}
{SAHPI_ENT_SYSTEM_CHASSIS, 1}
{SAHPI_ENT_ROOT, 0}
Example 2: SCSI Blade Expansion Module attached to blade in slot 3
{SAHPI_ENT_SYS_EXPANSION_BOARD, 3}
{SAHPI_ENT_SBC_BLADE, 3}
{SAHPI_ENT_PHYSICAL_SLOT, 3}
{SAHPI_ENT_SYSTEM_CHASSIS, 1}
{SAHPI_ENT_ROOT, 0}
Example 3: Management Module 2
{SAHPI_ENT_SYS_MGMNT_MODULE, 2}
{BLADECENTER_SYS_MGMNT_MODULE_SLOT, 2}
{SAHPI_ENT_SYSTEM_CHASSIS, 1}
{SAHPI_ENT_ROOT, 0}
Notes:
All HPI location values start at 1; except for the Virtual Management Module resource, which has an HPI location value of 0.
- HPI location numbers for the slot and the entity plugged into the slot are always equal.
- Although BladeCenter Blade Expansion Modules (BEMs) take up a blade slot themselves, a BEM's HPI location number always agrees with the location number of its host blade.
## Virtual Management Module
BladeCenter supports two dedicated Management Modules (MMs) which serve as the management control point for the entire chassis. The Management Modules plug into their own slots (they don't take up a blade slot) and are hot swappable. There must be at least one Management Module in the chassis for proper operations. The second MM is optional.
When the second MM is installed, it behaves as an active standby. The two Management Modules ping each other over an internal bus. If the primary MM fails, the standby takes over. With the exception of a few events, the takeover is completely automatic and transparent.
To model this behavior, BladeCenter supports a Virtual Management Module resource (VMM). It is distinguished by an HPI Entity Path location code of 0 (all physical resources have location codes starting with 1). The primary Management Module monitors the BladeCenter Event Log and several sensors. These are preserved over an MM failover and are associated with the VMM resource.
RDRs specific to an MM, like inventory, are associated with the individual physical MM resource.
## BladeCenter Model Resource Differences
The OpenHPI BladeCenter plugin dynamically determines what BladeCenter model it's communicating with and creates the necessary HPI entities. There isn't anything the HPI application need do or configure for this to happen. But just for fun, here's the major resource differences between the various BladeCenter models:

Resource	BladeCenter	BladeCenter H	BladeCenter T
Blades	14	14	8
I/0 Modules	4	10	4
Blowers	2	2	4

Table 2.3: BladeCenter Model Resource Differences

# Resource RDR Mappings
A couple of general BladeCenter RDR observations:
- HPI applications cannot disable individual sensors (e.g. SensorRec.EnableCtrl = SAHPI_FALSE for all sensors).
- HPI applications cannot disable individual events for a given sensor (e.g. SensorRec.EventCtrl = SAHPI_SEC_READ_ONLY for all sensors).
- HPI applications cannot set thresholds (e.g. SensorRec.ThresholdDefn.WriteThold = 0 for all threshold sensors).
- HPI applications cannot write inventory information. SA_ERR_HPI_READ_ONLY is returned for saHpiIdrAreaAdd(), saHpiIdrAreaDelete(), saHpiIdrFieldAdd(), and saHpiIdrFieldDelete() .
- To assist HPI applications in identifying individual voltage sensors, the Nominal value is defined to be the same as the voltage type (e.g. The 3.3 voltage sensor has a Nominal value of 3.3); else the HPI application needs to parse the RDR's IdString.
- For a complete description of how all the RDR fields are defined, refer to the OpenHPI file snmp_bc_resources.c.
## Chassis RDRs

Sensor	Type	Category	Events	Data Format
Ambient Air Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
I/O Module Redundancy	SAHPI_PLATFORM_ALERT	SAHPI_EC_REDUNDANCY	SAHPI_ES_FULLY_REDUNDANCY SAHPI_ES_REDUNDANT_LOST	Event only
Power Module Redundancy	SAHPI_PLATFORM_ALERT	SAHPI_EC_REDUNDANCY	SAHPI_ES_FULLY_REDUNDANCY SAHPI_ES_REDUNDANT_LOST	Event only
Power Domain 1 Redundancy	SAHPI_PLATFORM_ALERT	SAHPI_EC_REDUNDANCY	SAHPI_ES_FULLY_REDUNDANCY SAHPI_ES_REDUNDANT_LOST	Event only
Power Domain 2 Redundancy	SAHPI_PLATFORM_ALERT	SAHPI_EC_REDUNDANCY	SAHPI_ES_FULLY_REDUNDANCY SAHPI_ES_REDUNDANT_LOST	Event only
Chassis Total Maximum Power Capability	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Chassis Total Assigned Power	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Chassis Total Minimum Power Capability	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Chassis Filter (BCT only)	SAHPI_ENT_TEMPERATURE	SAHPI_EC_SEVERITY	SAHPI_ES_OK / SAHPI_ES_INFORMATIONAL / SAHPI_ES_MINOR_FROM_OK SAHPI_ES_MAJOR_FROM_LESS SAHPI_ES_CRITICAL	Event only

Table 3.1: Chassis Sensor RDR Summary

Control	Output Type	Type	Comments
Chassis Location LED (Writable Blue LED to illuminate / chassis location)	SAHPI_CTRL_LED	SAHPI_CTRL_TYPE_DISCRETE	0= Off; 1= solid on; 2=blinking

Table 3.2: Chassis Control RDR Summary

Inventory	Inventory Area Type	Supported Fields
Chassis Inventory	SAHPI_IDR_AREATYPE_CHASSIS_INFO	SAHPI_IDR_FIELDTYPE_CHASSIS_TYPE / SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_NAME / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_SERIAL_NUMBER / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.3: Chassis Inventory RDR Summary
## Slot RDRs
The Slot State sensor is a presence sensor which allows the HPI application to sense if there is something plugged into a physical slot. If there is a resource in the slot, the Slot State sensor returns an event state of SAHPI_ES_PRESENT and the Resource ID (RID) of the occupying resource. The RID is returned in the least significant 32 bits of an SAHPI_SENSOR_READING_TYPE_UINT64 value. The most significant 32 bits of the UINT64 value are set to 0. If there is no resource in the slot, an event state of SAHPI_ES_ABSENT and a RID of SAHPI_UNSPECIFIED_RESOURCE_ID is returned.
The Maximum Power Capability sensor reports the maximum power that the resource plugged into the slot could consume if it was fully populated (CPUs, memory chips, expansion cards, etc). The Assigned Power Capability sensor reports the power currently being supplied to the slot for its resource. The Minimum Power Capability sensor reports the minimum power that can be allocated to the slot's resource based on the resource's maximum CPU throttling capabilities.
Sensor	Sensor Number	Type	Category	Events	Data Format
Slot State	BLADECENTER_SENSOR_NUM_SLOT_STATE	SAHPI_ENTITY_PRESENCE	SAHPI_EC_PRESENCE	None	UINT64 (RID)
Slot Maximum Power Capability	BLADECENTER_SENSOR_NUM_MAX_POWER	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Slot Assigned Power	BLADECENTER_SENSOR_NUM_ASSIGNED_POWER	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Slot Minimum Power Capability	BLADECENTER_SENSOR_NUM_MIN_POWER	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)

Table 3.4: Slot Sensor RDR Summary
### Multi-slot Blades
In BladeCenter, blades may span multiple slots. In this case, each Slot State sensor in the slot span reports that the slot is occupied and returns the same RID. Blades are the only resource that span multiple slots.
For multi-slot blades, the Maximum, Assigned, and Minimum Power Capability values are spread evenly among the slots.
### Special Sensor Numbers
The sensor numbers for Slot RDRs are hard coded and defined in the OpenHPI file SaHpiBladeCenter.h. These sensor numbers are the same as those defined in the HPI-to-AdvancedTCA Mapping Specification (which defines similar sensors). The attempt is to provide the HPI application that needs to support both BladeCenter and ATCA chassis with as consistent an interface as possible.
### Power Module Slot RDRs
Generally the Power Module Slot resource reports 0 for the Power Module's Slot Maximum, Assigned, and Minimum Power Capability Sensors. In some BladeCenter models, the power modules themselves consume power. For example, the BladeCenter H power modules contain fan packs which cool the power modules. These fan packs draw current. The amount of which is reported by the Power Module's Slot Maximum, Assigned, Minimum sensors.
## Management Module RDRs
### Virtual Management Module RDRs
The VMM Redundancy sensor is an event only sensor that notifies the HPI application that MM redundancy has been lost or recovered.
The Active MM and Standby MM sensors returns and event state of SAHPI_ES_PRESENT and the Resource ID of the physical MM that serves as the active or standby MM. The RID is returned in the least significant 32 bits of an SAHPI_SENSOR_READING_TYPE_UINT64 value. The most significant 32 bits of the UINT64 value are set to 0. If there is no standby MM, the Standby MM sensor returns SAHPI_UNSPECIFIED_RESOURCE_ID and an event state of SAHPI_ES_ABSENT.
The MM Air Temperature sensor reads the temperature as recorded at the primary MM.
A variety of sensors monitor the voltage distribution coming from the power modules and being distributed in the chassis to the various hardware components.
A variety of sensors monitor internal chassis I2C buses used to determine the presence and status of various hardware components. Events from these sensors don't always mean that the component has failed; just that the primary MM cannot access it.
A control is provided to allow the HPI application to force a MM failover. Setting a value of SAHPI_CTRL_STATE_PULSE_ON forces the failover. This control returns SA_ERR_HPI_INVALID_REQUEST if there are not redundant MMs in the chassis. SAHPI_CTRL_STATE_OFF is always returned if the control's state is read.
Sensor	Type	Category	Events	Data Format
System Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SHAPI_ES_DEGRADED SAHPI_ES_OFF_LINE	Event Only
MM Redundancy	SAHPI_OPERATIONAL	SAHPI_EC_REDUNDANCY	SAHPI_ES_FULLY_REDUNDANT SAHPI_ES_NON_REDUNDANT_SUFFICIENT_RESOURCES	Event only
Active MM	SAHPI_ENTITY_PRESENCE	SAHPI_EC_PRESENCE	None	UINT64 (RID)
Standby MM	SAHPI_ENTITY_PRESENCE	SAHPI_EC_PRESENCE	None	UINT64 (RID)
MM Air Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR	UINT64 (Degrees C)
System 1.8 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
System 2.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
System 3.3 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
System 5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
System -5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
System 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_CRIT	FLOAT64 (Volts)
Midplane Maximum Power Capability	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Midplane Assigned Power	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)
Midplane Minimum Power Capability	SAHPI_OTHER_UNITS_BASED_SENSOR	SAHPI_EC_THRESHOLD	None	UINT64 (Watts)

Table 3.5: VMM Sensor RDR Summary

Control	Output Type	Type	Comments
MM Failover	SAHPI_CTRL_GENERIC	SAHPI_CTRL_TYPE_DIGITAL	SAHPI_CTRL_STATE_PULSE_ON Forces MM failover

Table 3.6: VMM Control RDR Summary

### Physical Management Module RDRs

Inventory	Inventory Area Type	Supported Fields
MM Inventory	SAHPI_IDR_AREATYPE_BOARD_INFO	SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.7: Physical MM Inventory RDR Summary

## Blade RDRs
Sensor	Type	Category	Events	Data Format
Blade Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE / SAHPI_ES_DEGRADED SAHPI_ES_INSTALL_ERROR	INT64 / 0 = unknown / 1 = good / 2 = warning / 3 = bad / 4 = kernelmode / 5 = discovering / 6 = comm error / 7 = no power / 8 = flashing / 9 = init error
Blade Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
Blade NMI Status	SAHPI_CRITICAL_INTERRUPT	SAHPI_EC_STATE	SAHPI_ES_STATE_ASSERTED SAHPI_ES_STATE_DEASSERTED	Event Only
Blade CPU 1 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
Blade CPU 2 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
Blade CPU 3 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
Blade CPU 4 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
Blade CPU 1 Core Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade CPU 2 Core Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade CPU 3 Core Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade CPU 4 Core Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade VRM Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 0.9 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 1.2 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 1.2 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 1.25 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 1.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 1.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 1.8 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 1.8 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 2.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 2.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 3.3 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 3.3 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade -5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Standby 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Memory Bank 1 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_UPPER_MAJOR	FLOAT64 (Volts)
Blade Memory Bank 2 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_UPPER_MAJOR	FLOAT64 (Volts)
Blade Memory Bank 3 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_UPPER_MAJOR	FLOAT64 (Volts)
Blade Memory Bank 4 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
Blade Battery Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)

Table 3.8: Blade Sensor RDR Summary

Control	Output Type	Type	Comments
Blade Location LED (Writable Blue LED to illuminate / blade location)	SAHPI_CTRL_LED	SAHPI_CTRL_TYPE_DISCRETE	0 = Off; 1 = solid on; 2 = blinking
Blade BMC Reset	SAHPI_CTRL_GENERIC	SAHPI_CTRL_TYPE_DISCRETE	1 = reset BMC

Table 3.9: Blade Control RDR Summary

Inventory	Inventory Area Type	Supported Fields
Blade Inventory	SAHPI_IDR_AREATYPE_BOARD_INFO	SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_NAME / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_SERIAL_NUMBER / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.10: Blade Inventory RDR Summary

## Blade Expansion Module RDRs

Sensor	Type	Category	Events	Data Format
BEM Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
BEM Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	Event Only
BEM Voltage	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	Event Only
PEU2 Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
PEU2 1 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
PEU2 3.3 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
PEU2 5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
PEU2 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
PEU2 Standby 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
BIE Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT / SAHPI_ES_UPPER_MAJOR	FLOAT64 (Degrees C)
BIE 1.5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
BIE 3.3 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
BIE2 5 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)
PEU 12 Volt	SAHPI_VOLTAGE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_LOWER_MAJOR	FLOAT64 (Volts)

Table 3.11: BEM Sensor RDR Summary

## BEM DASD RDRs
Sensor	Type	Category	Events	Data Format
BEM DASD 1 Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
BEM DASD 2 Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
BEM DASD 3 Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only

Table 3.12: BEM DASD Sensor Summary

## I/O Module RDRs

Sensor	Type	Category	Events	Data Format
I/O Module Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	INT64 / 0 = unknown / 1 = good / 2 = warning / 3 = bad
I/O Module Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
I/O Module Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_CRIT SAHPI_ES_UPPER_MAJOR	Event Only

Table 3.13: I/O Module Sensor RDR Summary

Inventory	Inventory Area Type	Supported Fields
I/O Module Inventory	SAHPI_IDR_AREATYPE_BOARD_INFO	SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.14: I/O Module Inventory RDR Summary
## Power Module RDRs

Sensor	Type	Category	Events	Data Format
Power Module Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	INT64 / 0 = unknown / 1 = good / 2 = warning / 3 = bad
Power Module Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
Power Module Temperature	SAHPI_TEMPERATURE	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR SAHPI_ES_UPPER_CRIT	Event Only
Power Module Fan Pack Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
Power Module Fan Pack Average Speed (Percent of Max) / (BCH only)	SAHPI_FAN	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR	PERCENTAGE
Power Module Fan Pack Average RPM Speed / (BCH only)	SAHPI_FAN	SAHPI_EC_UNSPECIFIED	None	FLOAT64 (RPM)

Table 3.15: Power Module Sensor RDR Summary

Inventory	Inventory Area Type	Supported Fields
Power Module Inventory	SAHPI_IDR_AREATYPE_BOARD_INFO	SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.16: Power Module Inventory RDR Summary

## Blower RDRs

Sensor	Type	Category	Events	Data Format
Blower Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	INT64 / 0 = unknown / 1 = good / 2 = warning / 3 = bad
Blower Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only
Blower Speed (Percent of Max)	SAHPI_FAN	SAHPI_EC_THRESHOLD	SAHPI_ES_UPPER_MAJOR	PERCENTAGE
Blower RPM Speed / (BCH only)	SAHPI_FAN	SAHPI_EC_UNSPECIFIED	None	FLOAT64 (RPM)

Table 3.17: Fan Sensor RDR Summary

## Media Tray RDRs

Sensor	Type	Category	Events	Data Format
Media Tray Operational Status	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_DEGRADED	Event Only
Media Tray Management Bus Operational State	SAHPI_OPERATIONAL	SAHPI_EC_AVAILABILITY	SAHPI_ES_RUNNING SAHPI_ES_OFF_LINE	Event Only

Table 3.18: Media Tray Sensor RDR Summary

Inventory	Inventory Area Type	Supported Fields
Media Tray Inventory	SAHPI_IDR_AREATYPE_BOARD_INFO	SAHPI_IDR_FIELDTYPE_MFG_DATETIME / SAHPI_IDR_FIELDTYPE_MANUFACTURER / SAHPI_IDR_FIELDTYPE_PRODUCT_VERSION / SAHPI_IDR_FIELDTYPE_PART_NUMBER

Table 3.19: Media Tray Inventory RDR Summary

# Hot Swap Operations
BladeCenter hardware currently supports two hot swap models.
- Simple “Not present or Active” model
- Three State “Not present, Inactive, Active” model
## Simple Hot Swap
Resources such as fans, power supplies, and the media tray become active as soon as they are installed into the system. There is no HPI application action required to activate these resources. Nor is there any action required to make these resources ready to be removed. These resources are modeled using HPI's Simplified Hot Swap model. HPI hot swap events are generated whenever the resource is removed from or installed into the system.
Resources supporting HPI's Simplified Hot Swap model are distinguished in Table 2.1: BladeCenter Resources by a Capabilities definition that includes SAHPI_CAPABILITY_FRU but does not include SAHPI_CAPABILITY_MANAGED_HOTSWAP.
## Three State Hot Swap
Resource such as blades, I/O modules, and Management Modules go through a three stage hot swap procedure – Not Present, Inactive, Active. When one of these resources is inserted into the chassis, it enters the Inactive state. In this state, the resource is in communication with the primary Management Module and has run self-tests to verify that it is ready for normal operations. It now takes an explicit action to activate the resource – either by pressing a local power-on hardware button or by issuing a remote power-on command. Likewise the resource can be power-off either locally or remotely to move the resource from the Active to the Inactive state. The resource can also be reset remotely – which acts like a power off/power on sequence.
So how to model this in HPI? HPI's Simplified Hot Swap model is too simple; while HPI's 5-state Managed Hot Swap model is too complex. To give HPI applications control over transitions between the Active and Inactive state, these resources are modeled using HPI's Managed Hot Swap model. The difference is that transitions from the Inactive state to the Active state and vice versa pass automatically through the HPI “Insertion Pending” and “Extraction Pending” states. See the figure below:

Active

Power Off
Power On

Insertion
Pending
Extraction
Pending
Automatic Transition States

Inactive
Power On
Power Off

Remove
Install

Not Present

For example, when a blade is inserted into the chassis, it enters into the HPI Inactive state. An informational HPI hot swap event flows to the HPI application marking the transition from SAHPI_HS_STATE_NOT_PRESENT to SAHPI_HS_STATE_INACTIVE. If the application then issues saHpiResourcePowerStateSet() to the blade, it will receive an informational hot swap event marking the transition from SAHPI_HS_STATE_INACTIVE to SAHPI_HS_STATE_INSERTION_PENDING followed immediately by another HPI event marking the transition from SAHPI_HS_STATE_INSERTION_PENDING to SAHPI_HS_STATE_ACTIVE. The automatic transitions through HPI's Insertion Pending and Extraction Pending states means:
- saHpiHotSwapPolicyCancel() always returns SA_ERR_HPI_INVALID_REQUEST
- saHpiResourceActiveSet() always returns SA_ERR_HPI_INVALID_REQUEST
- saHpiResourceInactiveSet() always returns SA_ERR_HPI_INVALID_REQUEST
- saHpiAutoInsertTimeoutGet() always returns SAHPI_TIMEOUT_IMMEDIATE
- saHpiAutoInsertTimeoutSet() always returns SA_ERR_HPI_READ_ONLY
- saHpiAutoExtractTimeoutGet() always returns SAHPI_TIMEOUT_IMMEDIATE
- saHpiAutoExtractTimeoutSet() always returns SA_ERR_HPI_READ_ONLY
BladeCenter blades, I/O modules, and Management Modules do not possess hot swap indicator LEDs so:
- saHpiHotSwapIndicatorStateGet() always returns SA_ERR_HPI_CAPABILITY
- saHpiHotSwapIndicatorStateSet() always returns SA_ERR_HPI_CAPABILITY
The HPI application may get HPI events re-announcing a state. For example, when in ACTIVE state, BladeCenter may generate another hot swap event stating that its in the ACTIVE state. Such re-announcements are informational and carry matching values for previous and current state.

# Event Processing
HPI defines a simple polling interface for events. Internally, however, things get a little complex. There are actually four major logs that are involved in the processing of events:
- BladeCenter Hardware Event Log
- OpenHPI BladeCenter Plugin Resource Event Log
- OpenHPI Domain Event Log
- OpenHPI Domain Alarm Table
## BladeCenter Hardware Event Log
At the base, is the BladeCenter's Hardware Event Log. This log is persistent in the BladeCenter hardware and is preserved over MM failovers and failures. All the noteworthy (plus some not so noteworthy) events in the BladeCenter system are logged here. The log is accessible externally through SNMP commands.
In a simplified event flow, an HPI application issues saHpiEventGet() which flows through the OpenHPI Infrastructure code to the OpenHPI BladeCenter plugin code. The OpenHPI BladeCenter plugin code issues an SNMP command to the BladeCenter Management Module to retrieve an event from the BladeCenter's Hardware Event Log. The BladeCenter event is then translated into an HPI event and returned the event to the OpenHPI Infrastructure code. The OpenHPI Infrastructure code then logs the event in its Domain Event Log, so that its available to all subscribed users. If the severity is high enough, the event is also logged to the Domain Alarm Table.
All HPI Resource Event Log commands, saHpiEventLogxxx(), deal with the BladeCenter Hardware Log and its characteristics and are supported by the OpenHPI BladeCenter plugin code.
All HPI Domain Event Log commands, saHpiEventGet() and saHpiEventAdd(); and all HPI Domain Alarm Table commands, saHpiAlarmxxx(), are supported entirely by the OpenHPI Infrastructure code. More on these in a bit.
### Non-Writable
The BladeCenter Hardware Event Log is not writable from external sources. SA_ERR_HPI_INVALID_CMD is returned for the command saHpiEventLogEntryAdd().
The HPI Infrastructure code, however, does support writable user-defined events to the Domain Event Log and the Domain Alert Table. So the commands SaHpiEventAdd() and SaHpiAlarmAdd() are supported.
### Variable Length
The BladeCenter Hardware Event Log is variable in size. The size varies depending upon what specific events are logged. Some are larger than others. Typically the number of events range from around 350 to almost 800 events. HPI assumes fix length logs so the OpenHPI BladeCenter plugin fibs a bit and returns a value of 768 for the maximum length of the log. 768 is based on the smallest BladeCenter event message.
### Wrap Characteristics
When the BladeCenter Hardware Event Log gets full, it wraps. The oldest events are replaced with the newer ones. Generally this isn't a problem, as we'll see, since the OpenHPI BladeCenter plugin code keeps a copy of the BladeCenter Hardware Event Log in its memory – which does not wrap. So events that are replaced in the hardware event log are generally still available in the plugin's memory cache.
### Too Much Stuff
Lots of stuff is logged in the BladeCenter's Hardware Event Log – not all of it useful to HPI applications or easily translated into HPI structures. However, no event in the hardware event log is lost or ignored. If the BladeCenter plugin code doesn't know what to do with an event (or doesn't think its useful), it translates the event into an HPI OEM event with the event's message put into the Text Buffer of the OEM event. An application could parse the Text Buffer of OEM events if desirable; but ,in general, HPI applications should simply ignore HPI OEM events.
A list of the hardware events explicitly mapped into non-OEM HPI events are listed in the OpenHPI file – snmp_bc_events.map.
## OpenHPI BladeCenter Resource Event Log
HPI's Resource Event Log (REL) for BladeCenter is supported in the OpenHPI's BladeCenter plugin code. The REL is associated with the Virtual Management Module resource. The plugin code keeps the REL synchronized with the BladeCenter Hardware Event Log .
To improve performance, the OpenHPI BladeCenter plugin code generally reads more than one event from the BladeCenter Hardware Event Log at a time. When an HPI application requests an event, the BladeCenter plugin determines if there are any new events to read from the hardware. If there are, the plugin reads all the new events in the BladeCenter Hardware Event Log at once. It stores the new events in the REL and feeds them to the OpenHPI Infrastructure code. If there are no new events to be read from the hardware but there are unprocessed events in the REL, the event is returned from the REL memory. This improves SNMP network efficiencies and reduces the chances that events are lost due to the hardware log wrapping.
### Initial Bring-up
The first time HPI comes up, the BladeCenter plugin code reads all of the BladeCenter's Hardware Event Log to create the REL. This may take a very long time (minutes) - there can be hundreds of events to read. There are a couple of things one can do to improve bring-up performance:
- Clear the Event Log before requesting the first event
  Issuing saHpiEventLogClear() causes the BladeCenter Hardware Event Log to be cleared. If course, you'll lose historical data (which may be stale).
- Use SNMP v3 and configure the “count_per_getbulk” variable in openhpi.conf to be as large as possible. Using SNMP GET-BULK commands to retrieve the initial set of events can dramatically reduce bring-up time. The maximun value for “count_per_getbulk” depends on the Management Module code level. Consult openhpi/plugins/snmp_bc/README for the details.
Besides performance, the other area of concern is stale data. When the BladeCenter Hardware Event Log is first read, it can contain events for resources that are no longer in the chassis (e.g. removed blades). The OpenHPI BladeCenter plugin code won't propagate events to the OpenHPI Infrastructure code until after the initial bring-up and discovery is finished. If the HPI application wants to read historical data, it can issue saHpiEventLogGet(); if it just wants events after bring-up, it can issue saHpiEventGet().
## OpenHPI Domain Event Log
This is the log that the HPI application reads when issuing saHpiEventGet(). Events can be added to this log using saHpiEventAdd().
Generally the OpenHPI Domain Event Log and the plugin's REL have more events then the application has read. When the application requests an event, it can usually be retrieved from memory instead of having to request the event from the hardware. This greatly improves performance. OpenHPI can also be configured to run in a threaded mode. In this mode, a separate thread polls the plugins for events every 3 seconds. The idea is to off-load the time getting and translating events directly from the hardware.
This design should also reduce concern about log wrapping. Unless the hardware event log can be overflown in 3 seconds, events will be picked up and saved in memory until the HPI application gets around to processing them. The amount of memory used to store events can be capped by the user, if desired, through the OPENHPI_EVT_QUEUE_LIMIT configuration option in openhpi.conf.

## OpenHPI Domain Alarm Table
For events with severities greater than or equal to SAHPI_MINOR, the OpenHPI Infrastructure code stores and tracks in the Domain Alarm Table (DAT). As events are recovered, they are removed from this table. User applications can add events to the DAT with the command – saHpiAlarmAdd(). The size of the DAT can be limited, if desired, by the OPENHPI_DAT_SIZE_LIMIT configuration option in openhpi.conf.